## Doc (full) (hidden)
Consultant: |  |  |  | Project: |  |  |  |  | Supplier: |  | Client:
Middle East Industry Standard Engineering Company |  |  |  | Iranian Babak Copper Company 50,000 TPA BIO-LEACHING/SX/EW PLANT PROJECT |  |  |  |  | EPCM Services Co.
Contract Number: 1013 |  |  |  | #REF! |  |  |  |  | #REF! |  | Sheet: 3
Contractor Job Number: C592 |  |  |  | #REF! |  |  |  |  | #REF!
#REF!
| Tag # | P&ID | Location |  | Flow (m³/hr) | S.G | Temp °C | Instrument Type |  | CV delta P |  | Range
| 400-PI-0001 A/B | 193-P-3040 | 400-PU-006 / 400-PU-007 |  | 500 | 1.2 | 25 | PRESSURE INDICATOR |  | N/A |  | 0-600 kPa
| 400-LE-0001 | 193-P-3040 | 400-TK-003 |  |  | 1.2 | 80 | LEVEL ELEMENT |  |  |  | 0-25 m
| 400-LI-0001 | 193-P-3040 | 400-TK-003 |  |  | 1.2 | 80 | LEVEL INDICATOR TRANSMITTER |  |  |  | 0-25 m
| 400-XPB-0001 AB | 193-P-3040 | 400-PU-006 |  |  |  |  | PUSHBUTTON STATION
| 400-XPB-0001 BB | 193-P-3040 | 400-PU-007 |  |  |  |  | PUSHBUTTON STATION
| 400-AE-0010 | 193-P-3041 | 400-CW-DN200-0001-S1-IJ |  | 345 | 1.2 |  | CONDUCTIVITY INSTRUMENT |  |  |  | ??
| 400-AIT-0010 | 193-P-3041 | 400-CW-DN200-0001-S1-IJ |  | 345 | 1.2 |  | CONDUCTIVITY INDICATOR TRANSMITTER |  |  |  | ??
| 400-ASA-0010 | 193-P-3041 | 400-CW-DN200-0001-S1-IJ |  |  |  |  | CONDUCTIVITY SWITCH ALARM
| 400-XV-0010 | 193-P-3041 | 400-CW-DN200-0001-S1-IJ |  | 345 | 1.2 |  | ACTUATED BALL VALVE
| 400-XZSC-0010 | 193-P-3041 | 400-XV-0010 |  |  |  |  | LIMIT SWITCH CLOSED
| 400-XZSO-0010 | 193-P-3041 | 400-XV-0010 |  |  |  |  | LIMIT SWITCH OPEN
| 400-PDSH-0013 | 193-P-3041 | 400-HX-001 |  |  |  | 80 | DIFFERENTIAL PRESSURE SWITCH HIGH
| 400-PDSH-0014 | 193-P-3041 | 400-HX-002 |  |  |  | 100 | DIFFERENTIAL PRESSURE SWITCH HIGH
| 400-TI-0010 | 193-P-3041 | 400-SPE-DN300-0006-S1 |  | 518 | 1.1 | 38 | TEMPERATURE INDICATOR |  |  |  | 0-100 °C
| 400-TI-0011 | 193-P-3041 | 400-STE-DN300-0003-P2 |  | 500 | 1.2 | 30 | TEMPERATURE INDICATOR |  |  |  | 0-100 °C
| 400-TI-0013 | 193-P-3041 | 400-SPE-DN300-0007-S1 |  | 518 | 1.1 | 30 | TEMPERATURE INDICATOR |  |  |  | 0-100 °C
| 400-TI-0015 | 193-P-3041 | 400-STE-DN300-0007-P2 |  | 500 | 1.2 | 50 | TEMPERATURE INDICATOR |  |  |  | 0-100 °C
| 400-TI-0016 | 193-P-3041 | 400-SPE-DN300-0003-S1 |  | 518 | 1.1 | 48 | TEMPERATURE INDICATOR |  |  |  | 0-100 °C
| 400-TE-0012 | 193-P-3041 | 400-SPE-DN300-0006-S1 |  | 500 | 1.1 | 30 | TEMPERATURE ELEMENT |  |  |  | 0-100 °C
| 400-TE-0014 | 193-P-3041 | 400-STE-DN300-0003-P2 |  | 500 | 1.2 | 50 | TEMPERATURE ELEMENT |  |  |  | 0-100 °C
| 400-TE-0017 | 193-P-3041 | 400-STE-DN300-0003-P2 |  | 518 | 1.2 | 48 | TEMPERATURE ELEMENT |  |  |  | 0-100 °C
| 400-TE-0018 | 193-P-3041 | 400-TK-001 |  |  | 1.1 | 50 | TEMPERATURE ELEMENT |  |  |  | 0-100 °C
| 400-TIT-0012 | 193-P-3041 | 400-TE-0012 |  | 500 | 1.1 | 30 | TEMPERATURE INDICATOR TRANSMITTER |  |  |  | 0-100 °C
| 400-TIT-0014 | 193-P-3041 | 400-TE-0014 |  | 500 | 1.2 | 50 | TEMPERATURE INDICATOR TRANSMITTER |  |  |  | 0-100 °C
| 400-TIT-0017 | 193-P-3041 | 400-TE-0017 |  | 518 | 1.2 | 48 | TEMPERATURE INDICATOR TRANSMITTER |  |  |  | 0-100 °C
| 400-TIT-0018 | 193-P-3041 | 400-TE-0018 |  |  | 1.1 | 50 | TEMPERATURE INDICATOR TRANSMITTER |  |  |  | 0-100 °C
| 400-PI-0010 A/B | 193-P-3041 | 400-PU-004 / 400-PU-005 |  | 518 | 1.1 | 48 | PRESSURE INDICATOR |  | N/A |  | ??
| 400-PI-0011 A/B | 193-P-3041 | 400-PU-001 / 400-PU-002 |  | 760 | 1.1 | 50 | PRESSURE INDICATOR |  | N/A |  | ??
| 400-PI-0012 | 193-P-3041 | 400-PU-003 |  | 1260 | 1.1 | 50 | PRESSURE INDICATOR |  | N/A |  | ??
| 400-XPB-0010 AB | 193-P-3041 | 400-PU-004 |  |  |  |  | PUSHBUTTON STATION
| 400-XPB-0010 BA | 193-P-3041 | 400-PU-005 |  |  |  |  | PUSHBUTTON STATION
| 400-XPB-0011 AB | 193-P-3041 | 400-PU-001 |  |  |  |  | PUSHBUTTON STATION
| 400-XPB-0011 BA | 193-P-3041 | 400-PU-002 |  |  |  |  | PUSHBUTTON STATION
| 400-XPB-0012 B | 193-P-3041 | 400-PU-003 |  |  |  |  | PUSHBUTTON STATION
| 400-XPB-0013 | 193-P-3041 | 400-PU-010 |  |  |  |  | PUSHBUTTON STATION
| 400-FV-0010 | 193-P-3041 | 400-STE-DN300-0003-P2 |  | 500 | 1.2 | 30 | FLOW CONTROL VALVE |  | 70
| 400-FV-0011 | 193-P-3041 | 400-SA-DNXXX-0001-S3 |  |  | 1.2 | 30 | FLOW CONTROL VALVE |  | 70
| 400-FE-0010 | 193-P-3041 | 400-STE-DN300-0003-P2 |  | 500 | 1.2 | 30 | FLOW ELEMENT |  |  |  | 0-1000 m3/h
| 400-FE-0011 | 193-P-3041 | 400-SA-DNXXX-0001-S3 |  |  | 1.2 | 30 | FLOW ELEMENT |  |  |  | ?? m3/h
| 400-FIT-0010 | 193-P-3041 | 400-STE-DN300-0003-P2 |  | 500 | 1.2 | 30 | FLOW INDICATOR TRANSMITTER |  |  |  | 0-1000 m3/h
| 400-FIT-0011 | 193-P-3041 | 400-SA-DNXXX-0001-S3 |  |  | 1.2 | 30 | FLOW ELEMENT |  |  |  | ?? m3/h
| 400-TV-014 | 193-P-3041 | 400-HW-DNXXX-0001-S1-IJ |  | 345 | 1 | 80 | TEMPERATURE CONTROL VALVE |  | 70
| 400-LV-010 | 193-P-3041 | 400-HW-DNXXX-0020-S1-IJ |  |  | 1 |  | LEVEL CONTROL VALVE
| 400-LE-0010 | 193-P-3041 | 400-TK-001 |  |  | 1.1 | 50 | LEVEL ELEMENT |  |  |  | 0-50 m
| 400-LIT-0010 | 193-P-3041 | 400-TK-001 |  |  | 1.1 | 50 | LEVEL INDICATOR TRANSMITTER |  |  |  | 0-50 m
| 400-LSHL-0011 | 193-P-3041 | 400-SU-001 |  |  |  |  | LEVEL SWITCH HIGH/LOW
| 400-LZSC-0010 | 193-P-3041 | 400-LV-0010 |  |  |  |  | LIMIT SWITCH CLOSED
| 400-FV-0020 | 193-P-3042 | 400-STE-DN300-0013-P2 |  | 133 | 1.1 | 50 | FLOW CONTROL VALVE |  | 70
| 400-FZSC-0020 | 193-P-3042 | 400-FV-0020 |  |  |  |  | LIMIT SWITCH CLOSED
| 400-FE-0020 | 193-P-3042 | 400-STE-DN300-0013-P1 |  | 133 | 1.1 | 50 | FLOW ELEMENT |  |  |  | 0-500 m3/h
| 400-FT-0020 | 193-P-3042 | 400-FE-0020 |  | 133 | 1.1 | 50 | FLOW TRANSMITTER
| 400-FV-0030 | 193-P-3043 | 400-STE-DN300-0016-P2 |  | 630 | 1.1 | 50 | FLOW CONTROL VALVE |  | 70
| 400-FZSC-0030 | 193-P-3043 | 400-FV-0030 |  |  |  |  | LIMIT SWITCH CLOSED
| 400-FE-0030 | 193-P-3043 | 400-STE-DN300-0016-P2 |  | 630 | 1.1 | 50 | FLOW ELEMENT |  |  |  | 0-1000 m3/h
| 400-FT-0030 | 193-P-3043 | 400-FE-0030 |  | 630 | 1.1 | 50 | FLOW TRANSMITTER
| 400-FV-0040 | 193-P-3044 | 400-STE-DN300-0017-P2 |  | 630 | 1.1 | 50 | FLOW CONTROL VALVE |  | 70
| 400-FZSC-0040 | 193-P-3044 | 400-FV-0040 |  |  |  |  | LIMIT SWITCH CLOSED
| 400-FE-0040 | 193-P-3044 | 400-STE-DN300-0017-P2 |  | 630 | 1.1 | 50 | FLOW ELEMENT |  |  |  | 0-1000 m3/h
| 400-FT-0040 | 193-P-3044 | 400-FE-0040 |  | 630 | 1.1 | 50 | FLOW TRANSMITTER
| 400-FV-0050 | 193-P-3045 | 400-STE-DN300-0018-P2 |  | 630 | 1.1 | 50 | FLOW CONTROL VALVE |  | 70
| 400-FZSC-0050 | 193-P-3045 | 400-FV-0050 |  |  |  |  | LIMIT SWITCH CLOSED
| 400-FE-0050 | 193-P-3045 | 400-STE-DN300-0018-P2 |  | 630 | 1.1 | 50 | FLOW ELEMENT |  |  |  | 0-1000 m3/h
| 400-FT-0050 | 193-P-3045 | 400-FE-0050 |  | 630 | 1.1 | 50 | FLOW TRANSMITTER
| 400-PI-0060 A/B | 193-P-3046 | 400-PU-008 / 400-PU-009 |  | 19.3 | 1 | 48 | PRESSURE INDICATOR |  | N/A
| 400-XPB-0060 AB | 193-P-3046 | 400-PU-008 |  |  |  |  | PUSHBUTTON STATION
| 400-XPB-0060 BB | 193-P-3046 | 400-PU-009 |  |  |  |  | PUSHBUTTON STATION
| 400-XV-0060 | 193-P-3046 | 400-WW-DN80-0002-P2 |  | 19.3 | 1 |  | ACTUATED BALL VALVE
| 400-XZSC-0060 | 193-P-3046 | 400-XV-0060 |  |  |  |  | LIMIT SWITCH CLOSED
| 400-XZSO-0060 | 193-P-3046 | 400-XV-0060 |  |  |  |  | LIMIT SWITCH OPEN

## COVER SHEET
Client: |  | Project : |  | Designer:
Golgohar Iron & Steel Development Co.
CLIENT DOC NO: S-SM01-D-BOP-WWTP-SCH-IN-003 |  | BARSOO DOC NO: 157LUGU2070002-01 |  | Rev: 01
Document Title: |  | INSTRUMENT & CONTROL & ELECTRICAL CABLE LIST FOR TRANSFER LINE |  | Sheet: 1 OF 5
INSTRUMENT & CONTROL & ELECTRICAL CABLE LIST
FOR TRANSFER LINE
01 | 2026-June-27 | IFA | G.Zargar | F.Niknam | A.Monfared
A1 | 2026-May-02 | IFA | G.Zargar | F.Niknam | A.Monfared
REV. | DATE | DESCRIPTION | PREPARED | CHECKED | APPROVED

## Revised Page Index
Client: |  |  |  |  | Project : |  |  |  |  | Designer:
Golgohar Iron & Steel Development Co.
Rev: 01 |  |  |  |  | INSTRUMENT & CONTROL & ELECTRICAL CABLE LIST FOR TRANSFER LINE |  |  |  |  | Rev: 01
Revised Page Index
Page | Revision | [6 empty] | Page | Revision
| A1 | 01 | 02 | 03 | 04 | 05 | 06 |  | A1 | 01 | 02 | 03 | 04 | 05 | 06
1 | x | x
2 | x | x
3 | x | x
4 | x | x
5 | x | x

## TABLE OF CONTENTS
Client: |  | Project : | Designer:
Golgohar Iron & Steel Development Co.
Rev: 01 |  | INSTRUMENT & CONTROL & ELECTRICAL CABLE LIST FOR TRANSFER LINE | Rev: 01
TABLE OF CONTENTS
SHEET NO. | TITLE |  |  | REV.
1 | COVER SHEET |  |  | 01
2 | Revised Page Index |  |  | 01
3 | TABLE OF CONTENTS, REFERRENCE DOCUMENTS, ABBREVIATION & NOTES |  |  | 01
4 | Cable LIST |  |  | 01
5 | MTO |  |  | 01
REFERRENCE DOCUMENTS
ITEM | DOCUMENT TITLE |  |  | DOCUMENT NO.
1
ABBREVIATION
A: Analogue
D: Digital
P: Power
RIO: Remote I/O Panel
MCC: Motor Control Center
VTA: Vendor To Advice
NOTES
(1): The routing of cables between the MCC and the LCS of pumps PU‑06A and PU‑06B is considered from the RWTP Substation Building (Steelmaking Area). The cables will be routed
through the existing cable ladder and then through the new cable tray route.Noted that the supply of this cable tray is included in the Electrical documents/scope.
(2): This cable is routed from the RWTP Substation Building (Steelmaking Area) through the existing cable ladder and then via the "new cable tray" route to the pumping station.
From the cable tray in the pump station (above LCSs), the cable is routed to the underside of the UCP panel using a flexible conduit.
(3):A Tank Cable Tray is used along this route, which is shared for carrying the LIT, LS, and UV signal cables.
(4): The dimensions and quantities of the Tank Cable Tray are as follows: 300 mm wide galvanized cable tray, 55 meters of straight sections,Two L‑shaped bends for corner transitions, One T‑junction.
(5): A vertical cable tray (300mm width, 800mm length) is considered on the tank wall to guide the signal cables of the valves after exiting the ground from the Heavy Rigid PVC Conduit to the Tank Cable Tray.
(6): Clamps shall be wall‑mounted type suitable for installation on walls and shall be selected according to the pipe size.
(7): The quantity of “Clamps & Accessories” for installation of Galvanized pipes, includes one complete set of clamp with two screws and the corresponding wall plugs (rawl plugs) for every 1.5 meters.
(8):The installation bulk materials for the cable trays include one set of brackets, supports, and two anchor bolts (roll bolts) for every 1.5 meters of tray length.
(9): For Cable Tray details refer document : 157DEDG1540101-00
(10): Refer to document “<CONTROL & INSTRUMENT CABLE ROUTE FOR TRANSFER LINE>” for New cable tray specifications.
(11): Starting from the transmitter with flexible conduit, the cable runs up along the tank wall via galvanized conduit, passes over the tank roof, then descends along the opposite side of the tank and enters the manhole. From there, it follows the existing cable route (as shown in the Cable Route drawings) and continues to Panel CP‑03 located in the RO Kowsar Control Room.
(12): POWER cable and Signal cable of FIT-1003 shall be routed separately. Also, in cale trays and ladders these cables shall be seperated with standard distance.

## Cable List
Golgohar Iron & Steel Development Co.
REV:01 |  |  | INSTRUMENT & CONTROL & ELECTRICAL CABLE LIST FOR TRANSFER LINE |  |  |  |  | Page 4 of 5
Item | Cable Tag | From | To | Cable Size | Cable Type | Cable Code | Voltage | Cable Length(m) | Cable Tray | Gland Size | REMARK
1 | LIT-1003-UCP | LIT-1003 | UCP | 1P*1.5 mm2 | RE-Y(st)Y fl PiMF | ANALOGE | 300/500 V | 50 | NOTE (3) | M20
2 | LIT-1004-UCP | LIT-1004 | UCP | 1P*1.5 mm2 | RE-Y(st)Y fl PiMF | ANALOGE | 300/500 V | 50 | NOTE (3) | M20 | Rev: 01
3 | LS-1003-UCP | LS-1003 | UCP | 2C*1.5mm2 | RE-Y(st)Y fl | DIGITAL | 300/500 V | 50 | NOTE (3) | M20
4 | LS-1004-UCP | LS-1004 | UCP | 2C*1.5mm2 | RE-Y(st)Y fl | DIGITAL | 300/500 V | 50 | NOTE (3) | M20
5 | PS-1005A-UCP | PS-1005A | UCP | 2C*1.5mm2 | RE-Y(st)Y fl | DIGITAL | 300/500 V | 10 | - | M20 | 4C*spare
6 | PS-1005B-UCP | PS-1005B | UCP | 2C*1.5mm2 | RE-Y(st)Y fl | DIGITAL | 300/500 V | 7 | - | M20 | 4C*spare
7 | UV-1007-UCP | UV-1007 | UCP | 10C*1.5 mm2 | RE-Y(st)Y fl | DIGITAL | 300/500 V | 85 | NOTE (3), NOTE (5) | M32 | 4C*spare
8 | UV-1008-UCP | UV-1008 | UCP | 10C*1.5 mm2 | RE-Y(st)Y fl | DIGITAL | 300/500 V | 85 | NOTE (3), NOTE (5) | M32 | 4C*spare
9 | PU-06A-MCC | MCC | UCP | 16C*1.5 mm2 | RE-Y(st)Y fl | DIGITAL | 300/500 V | 142 | NOTE (2) | M40 | 2C*spare
10 | PU-06A-LCS | LCS | MCC | 10C*1.5 mm2 | RE-Y(st)Y fl | DIGITAL | 0/6/1KV | 130 | NOTE (1) | - | 4C*spare
11 | PU-06A-LCB-AMM | LCS | MCC | 3C*1.5 mm2 | RE-Y(st)Y fl | DIGITAL | 0/6/1KV | 130 | NOTE (1) | - | AMMETER
12 | PU-06B-MCC | MCC | UCP | 16C*1.5 mm2 | RE-Y(st)Y fl | DIGITAL | 300/500 V | 145 | NOTE (2) | M40 | 2C*spare
13 | PU-06B-LCS | LCS | MCC | 10C*1.5 mm2 | RE-Y(st)Y fl | DIGITAL | 0/6/1KV | 130 | NOTE (1) | - | 4C*spare
14 | PU-06A-LCB-AMM | LCS | MCC | 3C*1.5 mm2 | RE-Y(st)Y fl | DIGITAL | 0/6/1KV | 130 | NOTE (1) | - | AMMETER
15 | RO-INT-01 | RO KOWSAR | UCP | 6-core, 9/125 um | single-mode, armored | Fiber Optic (Profibus) | - | 1300 | - | PG13.5 | Interlocks: I-01, I-01-01, FIT-1003
16 | CE | UCP | Clean EARTH | 1×16 mm² | Cu, Green/Yellow, PVC insulated | EARTH | - | SITE RUN | SITE RUN | -
17 | PE | UCP | Protective EARTH | 1×16 mm² | Cu, Green/Yellow, PVC insulated | EARTH | - | 7 | - | -
18 | UCP UPS Power | UPS | UCP | 2*(3*2.5 mm2) | N2XY | POWER | 0/6/1KV | 2*5 | - | PG16
19 | UCP Normal Power | LP | UCP | 2*3*2.5 mm2 | N2XY | POWER | 0/6/1KV | 5 | - | PG16
20 | UPS Power | LP | UPS | 2*(3*2.5 mm2) | N2XY | POWER | 0/6/1KV | 2*5 | - | PG16
21 | HMI Power Supply | HMI | Non-UPS (UCP) | VTA | VTA | VTA | - | VTA | - | -
22 | HMI Network Cable | HMI | CPU (UCP) | VTA | VTA | Profibus | - | VTA | - | -
23 | PU06A-P-C | STEEL MAKING PLANT RO | TRANSFER LINE PUMP STATION PU06A | 3X16 mm2 | N2XY | POWER | 0/6/1KV | 130 | NOTE (9) | PG29
24 | PU06B-P-C | STEEL MAKING PLANT RO | TRANSFER LINE PUMP STATION PU06B | 3X16 mm2 | N2XY | POWER | 0/6/1KV | 130 | NOTE (9) | PG29
25 | FIT-1003-UCP | FIT-1003 | UCP | 1P*1.5 mm2 | RE-Y(st)Y fl PiMF | ANALOGE | 300/500 V | 130 | NOTE (11) | M20 | LOCATION: RO KOWSAR
26 | FIT-1003-UCP-PS | FIT-1003 | UCP | 3*1.5 mm2 | RE-Y(st)Y fl PiMF | POWER | 300/500 V | 130 | NOTE (11),(12) | M20 | LOCATION: RO KOWSAR

## MTO
Golgohar Iron & Steel Development Co.
REV:01 |  |  | INSTRUMENT & CONTROL & ELECTRICAL CABLE LIST FOR TRANSFER LINE |  |  |  | Page 5 of 5
Item | Cable Size | Cable Type | Cable Code | Voltage | Cable Length(m) | Cable Accessories
1 | 1P*1.5 mm2 | RE-Y(st)Y fl PiMF | ANALOGE | 300/500 V | 230 | PVC Conduite Heavy Rigid (size: 2") |  | 50 meters of straight PVC Conduite Heavy Rigid and 3*90⁰ ELBOW and 1*45⁰ELBOW
2 | 2C*1.5mm2 | RE-Y(st)Y fl | DIGITAL | 300/500 V | 87 | Clamps & Accessories |  | 65 sets (7) | Rev: 01
3 | 10C*1.5 mm2 | RE-Y(st)Y fl | DIGITAL | 300/500 V | 170 | Galvanized Pipe (m) (size:1/2") |  | 80 meters of straight Galvanized Pipe and 6*90⁰ Galvanized Elbow
4 | 16C*1.5 mm2 | RE-Y(st)Y fl | DIGITAL | 300/500 V | 287 | Galvanized Cable Tray with Cover (m) |  | 300 mm wide galvanized cable tray, 56 meters of straight sections,Two L‑shaped bends for corner transitions, One T‑junction. (4) , (5)
5 | 10C*1.5 mm2 | RE-Y(st)Y fl | DIGITAL | 0/6/1KV | 260 | Cable Tray installation bulk material |  | 40 sets
6 | 3C*1.5 mm2 | RE-Y(st)Y fl | DIGITAL | 0/6/1KV | 260 | Flexible Conduit (m) (size:3/4") |  | 40m
7 | 6-core, 9/125 um | single-mode, armored | Fiber Optic (Profibus) | - | 1300 | Flexible Conduit (m) (size:1 1/4") |  | 85 m
8 | 1×16 mm² | Cu, Green/Yellow, PVC insulated | EARTH | EARTH | SITE RUN | Gland Size M20 |  | 8
9 | 1×16 mm² | Cu, Green/Yellow, PVC insulated | EARTH | EARTH | 7 | Gland Size M32 |  | 2
10 | 3*2.5 mm2 | N2XY | POWER | 0/6/1KV | 25 | Gland Size M40 |  | 2
11 | 3×16 mm² | N2XY | POWER | 0/6/1KV | 260 | Gland Size PG13.5 |  | 1
12 | 3*1.5 mm2 | RE-Y(st)Y fl PiMF | POWER | 300/500 V | 130 | Gland Size PG16 |  | 3
[6 empty] | Gland Size PG29 |  | 2
NOTE: | [5 empty] | Galvanized Pipe (m) (size:3/4") |  | 30 meters of straight Galvanized Pipe and 2*90⁰ Galvanized Elbow
A: Analogue D: Digital P: Power RIO: Remote I/O Panel
MCC: Motor Control Center
Cable Tray width: 300mm