Technical Specification For Cable Tray, Ladder, Conduit & Accessories Bulk Material

| 00 | ISSUED FOR APPROVAL | M.KHAVARI | F.NIKNAM | A.MONFARED | 1405/02/08 |
| --- | --- | --- | --- | --- | --- |
| Rev. | DESCRIPTION | REVISED BY | CHECKED BY | APPROVED | APP DATE |

| TABULATION REVISED PAGES |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| SHEET | Rev.00 | Rev.01 | Rev.02 | Rev.03 | SHEET | Rev.00 | Rev.01 | Rev.02 | Rev.03 |
| 01 | X |  |  |  | 51 |  |  |  |  |
| 02 | X |  |  |  | 52 |  |  |  |  |
| 03 | X |  |  |  | 53 |  |  |  |  |
| 04 | X |  |  |  | 54 |  |  |  |  |
| 05 | X |  |  |  | 55 |  |  |  |  |
| 06 | X |  |  |  | 56 |  |  |  |  |
| 07 | X |  |  |  | 57 |  |  |  |  |
| 08 | X |  |  |  | 58 |  |  |  |  |
| 09 | X |  |  |  | 59 |  |  |  |  |
| 10 | X |  |  |  | 60 |  |  |  |  |
| 11 | X |  |  |  | 61 |  |  |  |  |
| 12 | X |  |  |  | 62 |  |  |  |  |
| 13 | X |  |  |  | 63 |  |  |  |  |
| 14 | X |  |  |  | 64 |  |  |  |  |
| 15 | X |  |  |  | 65 |  |  |  |  |
| 16 | X |  |  |  | 66 |  |  |  |  |
| 17 | X |  |  |  | 67 |  |  |  |  |
| 18 | X |  |  |  | 68 |  |  |  |  |
| 19 | X |  |  |  | 69 |  |  |  |  |
| 20 | X |  |  |  | 70 |  |  |  |  |
| 21 | X |  |  |  | 71 |  |  |  |  |
| 22 | X |  |  |  | 72 |  |  |  |  |
| 23 | X |  |  |  | 73 |  |  |  |  |
| 24 | X |  |  |  | 74 |  |  |  |  |
| 25 | X |  |  |  | 75 |  |  |  |  |
| 26 | X |  |  |  | 76 |  |  |  |  |
| 27 | X |  |  |  | 77 |  |  |  |  |
| 28 | X |  |  |  | 78 |  |  |  |  |
| 29 | X |  |  |  | 79 |  |  |  |  |
| 30 | X |  |  |  | 80 |  |  |  |  |
| 31 | X |  |  |  | 81 |  |  |  |  |
| 32 | X |  |  |  | 82 |  |  |  |  |
| 33 | X |  |  |  | 83 |  |  |  |  |
| 34 | X |  |  |  | 84 |  |  |  |  |
| 35 |  |  |  |  | 85 |  |  |  |  |
| 36 |  |  |  |  | 86 |  |  |  |  |
| 37 |  |  |  |  | 87 |  |  |  |  |
| 38 |  |  |  |  | 88 |  |  |  |  |
| 39 |  |  |  |  | 89 |  |  |  |  |
| 40 |  |  |  |  | 90 |  |  |  |  |
| 41 |  |  |  |  | 91 |  |  |  |  |
| 42 |  |  |  |  | 92 |  |  |  |  |
| 43 |  |  |  |  | 93 |  |  |  |  |
| 44 |  |  |  |  | 94 |  |  |  |  |
| 45 |  |  |  |  | 95 |  |  |  |  |
| 46 |  |  |  |  | 96 |  |  |  |  |
| 47 |  |  |  |  | 97 |  |  |  |  |
| 48 |  |  |  |  | 98 |  |  |  |  |
| 49 |  |  |  |  | 99 |  |  |  |  |
| 50 |  |  |  |  | 100 |  |  |  |  |

Table of Content

1.0	GENERAL	6

1.1	SCOPE	6

1.2	DOCUMENT PRIORITY	6

1.3	CONDITION OF OPERATION	6

1.4	Plant Location	6

1.5	Meteorological	6

1.6	Conditions of Operation	8

2.0	STANDARDS AND CODES	8

1.0.	CABLE TRAYS DESCRIPTION	8

1.1.	Features	8

1.2.	Ladder type cable trays	9

1.3.	Material of Construction	10

1.4.	Finishing	10

1.5.	Sizing	10

2.0.	CABLE TRAYS ARRANGEMENT	10

2.1.	General	10

2.2.	Clearances	11

2.3.	Supports	11

2.4.	Covers	11

2.5.	Fittings	11

3.0.	DRAWINGS AND DOCUMENTATION	12

4.0.	Types of Cable Trays & Accessories	13

4.1.	Cable Tray Element	13

a)	13

1.1.	Finishing	20

1.2.	Hot deep galvanizing after fabrication, galvanizing thickness shall be 57 micron (average) of zinc coating	20

1.3.	Height	20

1.4.	Suitable for cable tray height border 100 mm	20

1.5.	Accessories	20

1.6.	Stainless Steel Hardware with Bolts, nuts and washer used for fixing plate to ladder	20

1.7.	Finishing	20

1.8.	Hot deep galvanizing after fabrication, galvanizing thickness shall be 57 micron (average) of zinc coating	20

1.9.	Length	20

1.10.	200 mm	20

1.11.	Height	20

1.12.	Suitable for cable tray height	20

1.13.	Accessories	20

1.14.	Stainless Steel Hardware with Bolts, nuts and washer used for fixing plate to ladder	20

1.15.	Finishing	21

1.16.	Hot deep galvanizing after fabrication, galvanizing thickness shall be 57 micron (average) of zinc coating	21

1.17.	Length	21

1.18.	250 mm	21

1.19.	Height	21

1.20.	Suitable for cable tray height border 100 mm	21

1.21.	Accessories	21

1.22.	Stainless Steel Hardware with Bolts, nuts and washer used for fixing plate to ladder	21

1.23.	Finishing	21

1.24.	Hot deep galvanizing after fabrication, galvanizing thickness shall be 57 micron (average) of zinc coating	21

1.25.	Length	21

1.26.	270 mm	21

1.27.	Height	21

1.28.	Suitable for cable tray height border 100 mm	21

1.29.	Accessories	21

1.30.	Stainless Steel Hardware with Bolts, nuts and washer used for fixing plate to ladder	21

1.31.	Finishing	22

1.32.	Hot deep galvanizing after fabrication, galvanizing thickness shall be 57 micron (average) of zinc coating	22

1.33.	Length	22

1.34.	170 + 100 mm	22

1.35.	Height	22

1.36.	Suitable for cable tray height	22

1.37.	Accessories	22

1.38.	Stainless Steel Hardware with Bolts, nuts and washer used for fixing plate to ladder	22

4.2.	Cable Trays Cover And Accessories	22

4.3.	Cable Trays Accessories	31

4.4.	U Channel	34

GENERAL

SCOPE

This specification is prepared to cover the project Cable Trays & Ladders that located in the Project.

DOCUMENT PRIORITY

In case of conflict between documents, the order of precedence shall be:

- This Specification.

- Drawings and other technical documents.

- I.E.C. standards.

- Other standard and codes when I.E.C. publications have not yet been issued.

CONDITION OF OPERATION

All of the Electrical Equipment & Systems will be suitable for 24 hours, 7 days/week, and 365 days/year operation.

Site Conditions

Plant Location

The Site is located at Gol-E-Gohar Iron Ore Complex, situated in Sirjan, Province of Kerman in southern part of Islamic Republic of IRAN, approximately 285 km southwest of Kerman city and 335 km north of Bandar Abbas port, in a semi-desertic high plateau terrain, 1750 m above sea level, and flanked by mountains over 2500 m high trending northwest to southwest.

Meteorological

Ambient Temperature

| Max. Temperature: | +40 deg. C (Recorded) |
| --- | --- |
|  | +50 deg. C (Design) |
| Min. temperature: | -12 deg. C (Recorded) |
|  | -10 deg. C (Design) |
| Average temperature: | +15.9 deg. C (Design) |
| Wet bulb design temperature (summer): | +25 deg C |
| Relative Humidity: | Max. 70% |

Wind Velocity

According to National Iranian Code (6th revision):

Basic speed data:                                        130 Km/h

Basic pressure data:                                    0.845 KN/m2

Correction factor:

0 - 10 m: 2

10 - 20 m: 2.2

20 - 100 m: 2.4

Rainfall

Yearly 120 mm (average)

Monthly rainfall 260mm (Max)

Barometric Pressure

820 milliards

Geological Conditions

This data is belongs to the existing palletizing plant location. For the engineering the

contractor shall be study geotechnical conditions for the essential location according to the project plan.

Altitude: About 1,750 m above mean sea level

Soil bearing: approx. 20t/m²

Ground water level: approx. 60 m below ground level

Earthquake Load

Equipment in plant will be dimensioned including a safety calculation against earthquake according to the “Iranian Code for Seismic Resistant Design of Buildings

– Publication No. S253-2nd edition, autumn 1999” (“Iranian Regulations 2800”) and “Minimum

Design Loads for Building and Structures” (Iranian Regulations 519).

- Design base acceleration: 0.3·g

- Classification of Buildings: Group 2

- - Soil classification: soil type III-b

Conditions of Operation

All of the Electrical Equipment & Systems will be suitable for 24 hours, 7 days/week, 365 days/year operation.

STANDARDS AND CODES

| IEC 61537 | Cable management - Cable tray systems and cable ladder systems |
| --- | --- |
| ISO 1461 | Hot Dip Galvanized Coatings on Fabricated Iron and Steel Articles |

In case of any conflicts among the above-mentioned referenced documents and this specification, the more stringent requirement shall govern.

- CABLE TRAYS DESCRIPTION

  - Features

Ladder type cable trays shall consist of two side channels to which rungs shall be fastened by continuous welding; spacing between rungs shall be <300 mm.

Sharp edges and burrs capable of damaging cables shall be positively avoided.

Ladder type cable trays are applied only for Electrical.

To protected cables, for each side number of cable tray’s inside edge shall be 3 (totally 6). (as following figure)

  - Ladder type cable trays

Available inside depth shall be not less than 85 mm. Widths shall be either 300 or 600mm (inside available clear space). The side channel size of cable trays shall be 100x25x25 mm. Rung channel size for cable trays shall be 35x15x15mm, fully welded to side channels. Thickness of rungs shall be same as side channels.

Perforated trough type cable trays (for Instrumentation) – Available inside depth shall not be less than 100mm for 400 & 600 mm wide trays. The same shall not be less than 50mm for 200 mm and 300 mm wide trays. The side channel for cable trays shall be 100X12X12 mm for 600 mm and    400 mm trays and 50x12x12 mm for 300 and 200 mm trays.

Widths shall be 100/200/300/400/500/600 mm (inside available clear space).

Depth of connecting splice plates shall be suitable for ladder or perforated type cable trays height.

Metal cable trays shall be assembled by means of continuous welding or bolting. Riveting and spot welding are not allowed. In any case, welding and punching shall be carried out before galvanizing.

Horizontal and vertical elbows shall be continuous (without angles).

MV cables, LV cables and control cables shall be placed on separated cable trays/ladders by considering MV cables placed on lowest level and control cables placed on upper trays/ladders.

The cable tray (Ladder type) side channels shall be fabricated with minimum 2mm thickness.

The cable tray (Perforated type) thickness shall be minimum 2mm.

The cable tray covers shall be minimum 1.5 mm thick

  - Material of Construction

Ladder type cable trays shall be made from hot deep galvanized.

Perforated type cable trays for Instrumentation shall also be made from hot deep galvanized steel.

  - Finishing

Finishing for the hot deep galvanized steel trays - Hot deep galvanizing shall be done after fabrication; for carbon steel having thickness  2 mm, the minimum galvanizing thickness shall be 85 micron of Zinc coating.

  - Sizing

Cable trays shall be designed to support the loads specified in Inquiry. Anyway, in lack of other instructions, a mass of 200 N per linear meter and per 200 mm tray width shall be considered.

The maximum deflection of tray span shall be within 1/200 of the span.

Working load is intended as useful carrying capacity, in addition to the tray its own load. Contribution of rungs to withstanding it is deemed negligible.

In addition to the working (static) load (due to cables), concentrated live load equal to 900 N (equivalent to a man weight) shall be considered, in whichever location respect to supports, without the tray being permanently deformed.

Cable tray system shall be able to withstand the required loads, with a safety factor  1.5.

- CABLE TRAYS ARRANGEMENT

  - General

Trays arrangement shall allow an easy laying and removal of cables.

  - Clearances

Vertical and Horizontal clearances between cable trays shall be ensured as per the requirements.

A side clearance of 600 mm at least is required for accessibility; if clearance on one side is less than the required one, cable tray shall be considered as not accessible on this side.

  - Supports

The maximum distance between brackets shall be considered 1.5 m.

  - Covers

Cable trays may be provided in outdoor areas on topmost layer of the trays, where cables are likely to be exposed to direct sunlight and mechanical damage is likely to occur during maintenance activities.

The covers shall be arranged so as not to confine the heat generated by radiation from the cables.

Mounting of covers on cable trays shall be carried out by spacers, for cable ventilation reasons.

  - Fittings

Manufacturer shall supply, together with straight sections of cable trays, the following fittings:

- brackets and structural elements, horizontal and vertical elbows, reducers, tees, crosses, rigid connectors, expansion connectors, adjustable connectors, spacers;

- hardware as screws, nuts, washers;

- Accessories as conduit adapters, partitions, fasteners, slopes.

Quantity shall be stated in Material requisition; in case of lack of quantity in Material requisition about hardware, quantity to be supplied shall be enough for a proper assembling, with a reasonable quantity overestimation.

- DRAWINGS AND DOCUMENTATION

General Documentation requirements

Manufacturer shall supply documentation with complete information about:

- Type of material;

- Type of finishing (in particular galvanizing);

- Mass of tray in kg per meter;

- Maximum overall dimensions,

- Basic solutions (standard span; allowed working load) with specification

- About consequent deflection values;

- Assembling instructions with illustrations.

- List of applicable type test certificates

- Test report of FAT

All documents shall show the relevant purchase order number, item and manufacturers   references.

- Types of Cable Trays & Accessories

  - Cable Tray Element

Cable Tray Straight Element

Length of Cable Tray :3000 mm Standard Length

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### STP10 | #### STL10 |
| #### 200 mm | STP20 | STL20 |
| #### 300 mm | STP30 | STL30 |
| #### 400 mm | STP40 | STL40 |
| #### 500 mm | STP50 | STL50 |
| #### 600 mm | STP60 | STL60 |
| #### 700 mm | STP70 | STL70 |

Cable Tray tee Element

Working Depth : minimum 100 mm inside for perforated and 85 mm for ladder type

Radius (RAD): 600mm

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### TEP10 | #### TEL10 |
| #### 200 mm | TEP20 | TEL20 |
| #### 300 mm | TEP30 | TEL30 |
| #### 400 mm | TEP40 | TEL40 |
| #### 500 mm | TEP50 | TEL50 |
| #### 600 mm | TEP60 | TEL60 |
| #### 700 mm | TEP70 | TEL70 |

Cable Tray horizontal 90° bend Element

Working Depth : minimum 100 mm inside for perforated and 85 mm for ladder type.

Radius (RAD) : 600mm

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### HBP10 | #### HBL10 |
| #### 200 mm | HBP20 | HBL20 |
| #### 300 mm | HBP30 | HBL30 |
| #### 400 mm | HBP40 | HBL40 |
| #### 500 mm | HBP50 | HBL50 |
| #### 600 mm | HBP60 | HBL60 |
| #### 700 mm | HBP70 | HBL70 |

Cable Tray horizontal 45° bend Element

Working Depth : minimum 100 mm inside for perforated and 85 mm for ladder type.

Radius (RAD): 600mm

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### HBP10(45) | #### HBL10(45) |
| #### 200 mm | HBP20(45) | HBL20(45) |
| #### 300 mm | HBP30(45) | HBL30(45) |
| #### 400 mm | HBP40(45) | HBL40(45) |
| #### 500 mm | HBP50(45) | HBL50(45) |
| #### 600 mm | HBP60(45) | HBL60(45) |
| #### 700 mm | HBP70(45) | HBL70(45) |

Note: Cable tray horizontal 90 bend element can be similar to point 8.1.4

Cable Tray internal vertical 90° bend Element

Working Depth : minimum 100 mm inside for perforated and 85 mm for ladder type

Radius (RAD): 600mm

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### VBP10(I) | #### VBL10(I) |
| #### 200 mm | VBP20(I) | VBL20(I) |
| #### 300 mm | VBP30(I) | VBL30(I) |
| #### 400 mm | VBP40(I) | VBL40(I) |
| #### 500 mm | VBP50(I) | VBL50(I) |
| #### 600 mm | VBP60(I) | VBL60(I) |
| #### 700 mm | VBP70(I) | VBL70(I) |

Cable Tray external vertical 90° bend Element

Working Depth : minimum 100 mm inside for perforated and 85 mm for ladder type

Radius (RAD) : 600mm

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### VBP10(E) | #### VBL10(E) |
| #### 200 mm | VBP20(E) | VBL20(E) |
| #### 300 mm | VBP30(E) | VBL30(E) |
| #### 400 mm | VBP40(E) | VBL40(E) |
| #### 500 mm | VBP50(E) | VBL50(E) |
| #### 600 mm | VBP60(E) | VBL60(E) |
| #### 700 mm | VBP70(E) | VBL70(E) |

Cable Tray right reduction Element

| #### WIDTH1 to WIDTH2 | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 600mm-500 mm | #### RRP(60-50) | #### RRL(60-50) |
| #### 600mm-400 mm | #### RRP(60-40) | #### RRL(60-40) |
| #### 600mm-300 mm | #### RRP(60-30) | #### RRL(60-30) |
| #### 600mm-200 mm | #### RRP(60-20) | #### RRL(60-20) |
| #### 600mm-100 mm | #### RRP(60-10) | #### RRL(60-10) |
| #### 500mm-400 mm | #### RRP(50-40) | #### RRL(50-40) |
| #### 500mm-300 mm | #### RRP(50-30) | #### RRL(50-30) |
| #### 500mm-200 mm | #### RRP(50-20) | #### RRL(50-20) |
| #### 500mm-100 mm | #### RRP(50-10) | #### RRL(50-10) |
| #### 400mm-300 mm | #### RRP(40-30) | #### RRL(40-30) |
| #### 400mm-200 mm | #### RRP(40-20) | #### RRL(40-20) |
| #### 400mm-100 mm | #### RRP(40-10) | #### RRL(40-10) |
| #### 300mm-200 mm | #### RRP(30-20) | #### RRL(30-20) |
| #### 300mm-100 mm | #### RRP(30-10) | #### RRL(30-10) |
| #### 200mm-100 mm | #### RRP(20-10) | #### RRL(20-10) |
| #### Height of cable tray | #### 100 mm | #### 100 mm |

Cable Tray LEFT reduction Element

| #### WIDTH1 to WIDTH2 | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 600mm-500 mm | #### LRP(60-50) | #### LRL(60-50) |
| #### 600mm-400 mm | #### LRP(60-40) | #### LRL(60-40) |
| #### 600mm-300 mm | #### LRP(60-30) | #### LRL(60-30) |
| #### 600mm-200 mm | #### LRP(60-20) | #### LRL(60-20) |
| #### 600mm-100 mm | #### LRP(60-10) | #### LRL(60-10) |
| #### 500mm-400 mm | #### LRP(50-40) | #### LRL(50-40) |
| #### 500mm-300 mm | #### LRP(50-30) | #### LRL(50-30) |
| #### 500mm-200 mm | #### LRP(50-20) | #### LRL(50-20) |
| #### 500mm-100 mm | #### LRP(50-10) | #### LRL(50-10) |
| #### 400mm-300 mm | #### LRP(40-30) | #### LRL(40-30) |
| #### 400mm-200 mm | #### LRP(40-20) | #### LRL(40-20) |
| #### 400mm-100 mm | #### LRP(40-10) | #### LRL(40-10) |
| #### 300mm-200 mm | #### LRP(30-20) | #### LRL(30-20) |
| #### 300mm-100 mm | #### LRP(30-10) | #### LRL(30-10) |
| #### 200mm-100 mm | #### LRP(20-10) | #### LRL(20-10) |
| #### Height of cable tray | #### 100 mm | #### 100 mm |

Cable Tray CENTRAL reduction Element

| #### WIDTH1 to WIDTH2 | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 600mm-500 mm | #### CRP(60-50) | #### CRL(60-50) |
| #### 600mm-400 mm | #### CRP(60-40) | #### CRL(60-40) |
| #### 600mm-300 mm | #### CRP(60-30) | #### CRL(60-30) |
| #### 600mm-200 mm | #### CRP(60-20) | #### CRL(60-20) |
| #### 600mm-100 mm | #### CRP(60-10) | #### CRL(60-10) |
| #### 500mm-400 mm | #### CRP(50-40) | #### CRL(50-40) |
| #### 500mm-300 mm | #### CRP(50-30) | #### CRL(50-30) |
| #### 500mm-200 mm | #### CRP(50-20) | #### CRL(50-20) |
| #### 500mm-100 mm | #### CRP(50-10) | #### CRL(50-10) |
| #### 400mm-300 mm | #### CRP(40-30) | #### CRL(40-30) |
| #### 400mm-200 mm | #### CRP(40-20) | #### CRL(40-20) |
| #### 400mm-100 mm | #### CRP(40-10) | #### CRL(40-10) |
| #### 300mm-200 mm | #### CRP(30-20) | #### CRL(30-20) |
| #### 300mm-100 mm | #### CRP(30-10) | #### CRL(30-10) |
| #### 200mm-100 mm | #### CRP(20-10) | #### CRL(20-10) |
| #### Height of cable tray | #### 100 mm | #### 100 mm |

Separators (Dividers)

| #### Separators (Dividers) | #### Ladder Type: SPL #### Perforated Type: SPP |
| --- | --- |
| - Finishing | - Hot deep galvanizing after fabrication, galvanizing thickness shall be 57 micron (average) of zinc coating |
| - Height | - Suitable for cable tray height border 100 mm |
| - Accessories | - Stainless Steel Hardware with Bolts, nuts and washer used for fixing plate to ladder |

| #### Normal Joint For Ladder / perforated Type Cable Trays | #### Ladder / perforated Type: NJ |
| --- | --- |
| - Finishing | - Hot deep galvanizing after fabrication, galvanizing thickness shall be 57 micron (average) of zinc coating |
| - Length | - 200 mm |
| - Height | - Suitable for cable tray height |
| - Accessories | - Stainless Steel Hardware with Bolts, nuts and washer used for fixing plate to ladder |

Horizontal Hinged Splice Plate

| #### Horizontal Hinged Splice Plate | #### Ladder Type: HHSL #### Perforated Type: HHSP |
| --- | --- |
| - Finishing | - Hot deep galvanizing after fabrication, galvanizing thickness shall be 57 micron (average) of zinc coating |
| - Length | - 250 mm |
| - Height | - Suitable for cable tray height border 100 mm |
| - Accessories | - Stainless Steel Hardware with Bolts, nuts and washer used for fixing plate to ladder |

Vertical Hinged Splice Plate

| #### Vertical Hinged Splice Plate | #### Ladder Type: VHSL #### Perforated Type: VHSP |
| --- | --- |
| - Finishing | - Hot deep galvanizing after fabrication, galvanizing thickness shall be 57 micron (average) of zinc coating |
| - Length | - 270 mm |
| - Height | - Suitable for cable tray height border 100 mm |
| - Accessories | - Stainless Steel Hardware with Bolts, nuts and washer used for fixing plate to ladder |

Lateral Connection Joint

| #### Lateral Connection Joint | #### Ladder Type: LCJL |
| --- | --- |
| - Finishing | - Hot deep galvanizing after fabrication, galvanizing thickness shall be 57 micron (average) of zinc coating |
| - Length | - 170 + 100 mm |
| - Height | - Suitable for cable tray height |
| - Accessories | - Stainless Steel Hardware with Bolts, nuts and washer used for fixing plate to ladder |

  - Cable Trays Cover And Accessories

Cable Tray Straight Element Cover

| #### Length of each unit cover | #### 1500 mm standard length |
| --- | --- |

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### CSTP10 | #### CSTL10 |
| #### 200 mm | CSTP20 | CSTL20 |
| #### 300 mm | CSTP30 | CSTL30 |
| #### 400 mm | CSTP40 | CSTL40 |
| #### 500 mm | CSTP50 | CSTL50 |
| #### 600 mm | CSTP60 | CSTL60 |
| #### 700 mm | CSTP70 | CSTL70 |

Cable Tray External Vertical 90° Bend Element Cover

| #### Minimum Bending Radius | #### 600 mm (minimum bending radius of the cable tray) |
| --- | --- |

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### CVBP10(E) | #### CVPL10(E) |
| #### 200 mm | CVPP20(E) | CVPL20(E) |
| #### 300 mm | CVPP30(E) | CVPL30(E) |
| #### 400 mm | CVPP40(E) | CVPL40(E) |
| #### 500 mm | CVPP50(E) | CVPL50(E) |
| #### 600 mm | CVPP60(E) | CVPL60(E) |
| #### 700 mm | CVPP70(E) | CVPL70(E) |

Cable Tray Internal Vertical 90° Bend Element Cover

| #### Minimum Bending Radius | #### 600 mm (minimum bending radius of the cable tray) |
| --- | --- |

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### CVBP10(I) | #### CVPL10(I) |
| #### 200 mm | CVPP20(I) | CVPL20(I) |
| #### 300 mm | CVPP30(I) | CVPL30(I) |
| #### 400 mm | CVPP40(I) | CVPL40(I) |
| #### 500 mm | CVPP50(I) | CVPL50(I) |
| #### 600 mm | CVPP60(I) | CVPL60(I) |
| #### 700 mm | CVPP70(I) | CVPL70(I) |

Cable Tray Horizontal 45° Bend Element Cover

| #### Minimum Bending Radius | #### 600 mm (minimum bending radius of the cable tray) |
| --- | --- |

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### CHBP10(45) | #### CHPL10(45) |
| #### 200 mm | CHPP20(45) | CHPL20(45) |
| #### 300 mm | CHPP30(45) | CHPL30(45) |
| #### 400 mm | CHPP40(45) | CHPL40(45) |
| #### 500 mm | CHPP50(45) | CHPL50(45) |
| #### 600 mm | CHPP60(45) | CHPL60(45) |
| #### 700 mm | CHPP70(45) | CHPL70(45) |

Cable Tray Horizontal 90° Bend Element Cover

| #### Minimum Bending Radius | #### 600 mm (minimum bending radius of the cable tray) |
| --- | --- |

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### CHBP10(90) | #### CHPL10(90) |
| #### 200 mm | CHPP20(90) | CHPL20(90) |
| #### 300 mm | CHPP30(90) | CHPL30(90) |
| #### 400 mm | CHPP40(90) | CHPL40(90) |
| #### 500 mm | CHPP50(90) | CHPL50(90) |
| #### 600 mm | CHPP60(90) | CHPL60(90) |
| #### 700 mm | CHPP 70(90) | CHPL70(90) |

Cable Tray Tee Element Cover

| #### Minimum Bending Radius | #### 600 mm (minimum bending radius of the cable tray) |
| --- | --- |

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### CTEEP10 | #### CTEEL10 |
| #### 200 mm | CTEEP20 | CTEEL20 |
| #### 300 mm | CTEEP30 | CTEEL30 |
| #### 400 mm | CTEEP40 | CTEEL40 |
| #### 500 mm | CTEEP50 | CTEEL50 |
| #### 600 mm | CTEEP60 | CTEEL60 |
| #### 700 mm | CTEEP70 | CTEEL70 |

Cable Tray Right Reduction Element Cover

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### CRR10 | #### CRRL10 |
| #### 200 mm | CRRP20 | CRRL20 |
| #### 300 mm | CRRP30 | CRRL30 |
| #### 400 mm | CRRP40 | CRRL40 |
| #### 500 mm | CRRP50 | CRRL50 |
| #### 600 mm | CRRP60 | CRRL60 |
| #### 700 mm | CRRP70 | CRRL70 |

Cable Tray Left Reduction Element Cover

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### CLR10 | #### CLRL10 |
| #### 200 mm | CLRP20 | CLRL20 |
| #### 300 mm | CLRP30 | CLRL30 |
| #### 400 mm | CLRP40 | CLRL40 |
| #### 500 mm | CLRP50 | CLRL50 |
| #### 600 mm | CLRP60 | CLRL60 |
| #### 700 mm | CLRP 70 | CLRL70 |

Cable Tray Central Reduction Element Cover

| #### WIDTH | ITEM(Perforated type) | ITEM(Ladder type) |
| --- | --- | --- |
| #### 100 mm | #### CCR10 | #### CCRL10 |
| #### 200 mm | CCRP20 | CCRL20 |
| #### 300 mm | CCRP30 | CCRL30 |
| #### 400 mm | CCRP40 | CCRL40 |
| #### 500 mm | CCRP50 | CCRL50 |
| #### 600 mm | CCRP60 | CCRL60 |
| #### 700 mm | CCRP 70 | CCRL70 |

  - Cable Trays Accessories

Cover Fixing Clamp

| #### Cover Fixing Clamp | #### Ladder /Perforated Type: SC |
| --- | --- |
| #### Finishing | #### Electroplated zinc galvanized |
| #### Accessories | #### Head bolts, Nut & Washer included |

Horizontal Support

| #### Horizontal Support | #### Type: |
| --- | --- |
| #### Finishing | #### Hot deep galvanizing after fabrication, galvanizing thickness shall be 85 micron(average) of zinc coating |
| #### Length | #### Suitable for 300mm/400mm/600 wide cable tray and cable ducts |
| #### Height |  |

Bolt Fixing To Support (Beam)

| #### Bolt Fixing To support (Beam) | #### Type: |
| --- | --- |
| #### Finishing | #### Hot deep galvanizing after fabrication, galvanizing. |
| #### Accessories | #### Nut, plane washer and spring washer |

Bolt Fixing Cable Tray To Structure (Rack)

| #### Bolt Fixing Cable Tray To Structure (Rack) | #### Type: |
| --- | --- |
| #### Material of Construction | #### Carbon Steel |
| #### Finishing | #### Hot deep galvanizing after fabrication, galvanizing. |
| #### Accessories | #### Double plate, head bolts, nut and washer included |

Bolt Fixing Cable Tray To Brackets

| #### Bolt Fixing Cable Tray To Brackets | #### Type: |
| --- | --- |
| #### Finishing | #### Hot deep galvanizing after fabrication, galvanizing. |
| #### Accessories | #### Head bolts & nut included |

Ceiling Or Floor Fastening Plate (Simple Type)

| #### Ceiling Or Floor Fastening Plate | #### Type: |
| --- | --- |
| #### Finishing | #### Hot deep galvanizing after fabrication, galvanizing thickness shall be 85 micron(average) of zinc coating |
| #### Dimension | #### Suitable for single channel |
| #### Base plate | #### Base plate with welded “U” Steel plate |
| #### Accessories | #### Stainless Steel Hardware with Channel nut screw, washers and bolts and expansion bolts for support fixing |
| #### Height | #### L = 100mm |

Ceiling Or Floor Fastening Plate (Double Type)

| #### Ceiling Or Floor Fastening Plate (Double Type) | #### Type: |
| --- | --- |
| #### Finishing | #### Hot deep galvanizing after fabrication, galvanizing thickness shall be 85 micron(average) of zinc coating |
| #### Dimension | #### Suitable for double channel |
| #### Base plate | #### Base plate with welded “U” Steel plate |
| #### Accessories | #### Stainless Steel Hardware with Channel nut screw, washers and bolts and expansion bolts for support fixing |
| #### Height | #### L1 = 200mm |

  - U Channel

Thickness: min. 2.5mm